FanSave






  User’s Manual

Energy Savings Calculator

for Fan Drives

ACS55

ACS150

ACS310, ACS355

ACS550, ACH550, ACS580

ACS800, ACS880

[image: image12.jpg]



[image: image1.emf]


3AFE 64232681 REV M EN

Effective: 01.08.2012
Copyright © ABB Oy, Drives/TT
[image: image11.wmf] 


1 — General

FanSave is a tool running on Microsoft Excel to calculate the energy savings available when using ABB variable speed AC drive instead of other fan control systems.

Comparisons can be made with damper control, pitch control, single speed vane control and 2-speed vane control.

Calculations are based on typical fan operating characteristics.  Consequently, the accuracy of the results is limited.  The accuracy of the results is also affected by the accuracy of the input data.   The results of this program must not be used as the basis for guaranteed energy savings.

Results of calculations can be printed out.

Version 5.3


New general purpose drive ACS580 added. 

Version 5.1


Added three languages and now supported languages are Chinese, Dutch, English, Finnish, French, German, Portuguese, Russian and Vietnamese. 

Version 5.0

New industrial drive ACS880 added and the structure of worksheet changed from horizontal to vertical.   The data inputs are on one page and following page is report.  The vertical pages are supposed to be more user friendly supported by PageUp and PageDown of keyboard and scroll wheel of modern mouse. 

Additionally the internal computing are made modern way.   This anyway prevents the usage on older the 2007 Excels.  The US style is supported later with US version.  

2 — Starting and Running the Program

Software Required 

Microsoft® Excel 2007 or later is required to run the energy calculation workbook.  Also you shall enable the running of macros.  The permanent settings for this are on Excel options/Trust center/Trust center settings/Marco settings.

Files Provided 

The FanSave files for fan drive calculations are incorporated into Excel workbook named originally FanSave53.xls.

Installation

No installation is required but the workbook is can be copied to a hard disk and short-cut arranged to desktop.

Opening the Workbook

Start Excel as usual. For fan calculations open FanSave53.xls. 

You may adjust the Ribbon etc settings of Excel to get more space.

FanSave will open with zoom setting 100% to get overview of input page, but you may zoom later on according to your preferences.

Disclaimer

At the end worksheet is the important disclaimer statement. 

 [image: image2.png]License Agreement and Copyright Notice. ==

IMPORTANT - READ BEFORE COPYING, OPENING OR USING.

Do ot copy, open, or use the Calculaton Tool provided under this cense agreement (License’), unti you have carefuly
read the foloving terms and conditons.

By copying, opening, o o using the Calculation Tool, you agree to be bound by the terms of this License. If you do
ot agree to the tems of thisicense, do not copy, open, or use the Calcuation Too.

License Agreement and Copyright Notice

1488 hereby grants Licensee a non-exchusive, non-transferable, royalty-fee liense o use for information purposes, copy
and ditrbute this energy savings calculation tool(hereafter "Calculation Tool”) pubished by ABB in accordance with the
terms and condiions of this License. Al ntellctual property rihts and tte to the Calcuiation Tool shal remain with ABB and
nonterest or onnership therein i conveyed to Licnsee. No riht to modiy (even for purposes of error correcton), adapt,
decompie or translate the Calaation Tool o create derivative works therefrom i granted to Licensee. Except as expressly
provided for in thisLicense, o icense of right s granted to Licensee directly or by impication, inducement, estoppel or
othernse.

Permission to use for information purposes, copy and distribute this calculation tool publshed by ABB is hereby granted on
the conditon that each copy contains this License Agreement and Copyright Nofce in s entrety and that the use of this
calciation tool i restricted for information purposes only. Even though every effort has been made to ensure a sufficent
acauracy of the ress in  typica situation, the resuits given by ths Calulation Tool must not be perceived as guaranteed
energy savings.

Didaimer of Warranty. ALL INFORMATION, CALCULATIONS MADE AND RESULTS WITHINTHIS CALCULATION TOOL ARE
PROVIDED AS TS WITHOUT ANY REPRESENTATION OR WARRANTY OF ANY KIND EITHER EXPRESS OR MPLIED INCLUDING
BT NOT LIMITED TO IMPLIED WARRANTIES FOR MERGHANTABILITY, FITNESS FOR A PARTICULAR PLRPOSE OR NOK-
INFRINGEVENT. THIS TOOL AND ANY OTHER ABB DOCUMENTATION AY INCLUDE TECHNICAL INACCLRACEES OR
TYPOGRAPHICAL ERRORS. CHANGES AND ADDITIONS MAY BE MADE BY AB3 FROM TIVE TO TIWE TO ANY INFORMATION
CONTAINED HEREIN, THE LICENSEE I5 SOLELY RESPONSIBLE FOR DETERMINING THE APPROPRIATENESS OF LSING OR
DISTRIEUTING THE CALCULATION TOOL AND ASSUMES ANY RISKS ASSOCIATED WITH HIS EXERCISE OF PERMISSIONS
UNDER THIS LICENSE.

Limitation of Liabiity. In no event and under no legal theory, whether in tort (induding negligence), contract, or otherwise,
riess requre by applcabl o (such o delberate and rsly neglgent i), shal ABS be lable fr any damages, I
induing any direct, indirect, spegl ncident o consequentil damages of ay kind aisg as 2 resul of s License or

out of the use or inability to use the Calculation Tool (induding but not limited to damages for loss of goodwil, work
stoppage, computer fare o malfncton orany and l ther commerdal damages orosss), even f ASE hes been
advsed of th possbity of such damages.

© Copyright 1994-2005 ABB. Al rights reserved.

Taccept al the terms of this Agreement. o not accept the terms of this Agreement.





Worksheet

The language setting is on top right corner.   The translated words and help texts are taken from Language sheet based on English keywords.   This manual explains the English ones. 

[image: image3.png]English -

Chinese
Dutch
Finnish
French
German
Portuguese
Russian
Viethamese





The Worksheet print will print a two page report by default.

3 — FanSave worksheet inputs and results

General

All white fields on the sheet are for entering information and data Figure 1. 

The sheet is filled in by default values to help users to right away find the idea of worksheet. 

The Results are displayed on second page Figure 2.

[image: image4.png]FanSave 5.3  Energy saving calculator for fans

Fan

3

Norinatvoam fom

e 0
— S -
Transmission efficiency 10
i

BT e RN

Drive and motor
Suplyvoage v E
Requred motr power B4
Motrpover o

El
Wotor efcincy %

mproved cono by = -

Flow profle

Ji— | —
ciow ot

w5 we s
o 10 % B
ww A 5 one ey
T 20 %= m2m
wn B owe v
ww ] B one 9,
0w T we e
s E owe e
2% 0 u- on
sm w0 % ewon

[R——

Curey =

- T e

nvesiment cost 00 €
o2 emision funt 08 igrin




Figure 1 FanSave input page 

Input data 
The input data includes information about fan, transmission, existing control method, motor, operating profile.  

Economic data such as energy price and investment cost is required in order to get figures for investment appraisal.

Fan data

Nominal Volume Flow, Qvn (m3/s)

Enter the maximum system volume flow in cubic meters per second, which the existing system will deliver and fan must reach with existing control. FanSave will assume that exactly the same flow has to be delivered also with AC Drive.  The energy saving calculations will be based on flow rates that are equal to or less than Qvn.

Pressure Increase, ptF (Pa)

Required pressure increase of the fan for the given nominal volume flow Qvn. Value is determined from the fan curves and system curve intersection.

If pressure is more than 5000 Pa FanSave will indicate this by red color and 

It is better to compute these cases manually.  The computing of high pressure fans does not come correct because the compression of the gas cannot be simply modeled. 

Efficiency, ( (%)

Enter the nominal efficiency of the fan at nominal volume flow.

Transmission Efficiency, ( (%)

Efficiency of the transmission method e.g. belt transmission. If the fan has been connected directly to the motor, use 100%.

Fan type

Fan type can be selected. The options are centrifugal and axial flow. 

Impeller type

Centrifugal fans of different blade shapes behave differently. The options for impeller type are forward curved, backward curved, and radial blades.
Existing Flow Control

Pick the existing control method that you want to compare with ABB AC Drive control. The control method is selected from the drop-down list on the upper left part of the sheet. The control options are: Outlet damper, Slip coupling, Voltage,Two-speed motor, Cyclic (on/off), Inlet box damper, Inlet vanes, ( 1-speed vane, 2-speed vane and Pitch control). 

The smaller energy usage of frequency converter is compared to a large energy required by: 

Outlet damper control which control the volume flow by throttling it with a damper.

Slip coupling which control the fan speed with slippage by hydraulic/eddy current technology.

Voltage control which will make the motor voltage lower and make the induction motor to have larger slip. Note! Voltage control is applicable only for fans with lower unit powers (< 3kW)

Two speed motor (two sets of windings 1:2/Dahlander connection) which means larger motor compared to one speed motor.

Cyclic (on/off) which means ON/OFF duty is adjusted according to flow requirements and it is acceptable from application point of view.  The control can’t be as good as with speed control.   When motor and fan are running they run at full speed.
Inlet box damper is based on damper control.
Pitch adjustment for axial fans / Inlet vanes for centrifugal fans
Vane control is done by inlet vane installed at the fan inlet.

Pitch control is by adjusting the pitch angle of axial-flow fan.

Drive and motor data

Supply voltage

Enter the reference supply voltage to be used.  The value should be between 115 (1-ph) to 690 V (3-ph).  This is used to screen out drive types. 

Required motor power
FanSave is computing from fan data the required motor output power including 10% thermal margin.  Based on this number you shall enter the Motor power. 

Motor power (kW)

Enter the nameplate power rating of the motor. This is used to select the proper drive rating.  The program uses calculated power demand to determine energy savings.  

Motor efficiency, (m (%)

Enter the motor efficiency from the motor nameplate or from other data supplied by the motor manufacturer. Use the efficiency for full load operation on fixed frequency utility power. The program will adjust the efficiency for operation at reduced speeds and loads. If the motor is oversized for the application, enter the efficiency for operation at the maximum applied load.

Improved control by

User should select the drive family from drop down box.  FanSave will pick the drive rating based on motor power and voltage.

Flow profile

Annual running time

In other words, this is the total operating time per year. Enter the estimated number of hours that the fan is expected to run during a year’s time. For 24 hour, 365-day operation, enter 8760 hours.

Operating Time at Different Flow Rates (%)

Enter the estimated time as a percentage of the total operating time for operation at each of the listed flow rates from 100% to 20%.  Enter zero for flow rates that are not used. The sum of the entered percentages shall be 100%. A figure under the white cells show the sum. If it is not 100, a comment “Sums must equal 100%” is shown.

Economic Data

Currency unit

Specify here the currency to be used in calculations.

Energy price (per kWh)

Enter the price of energy per kilowatt-hour (kWh). The FanSave program does not have provisions for calculating demand charges. To estimate energy cost including demand charges, enter the average cost of energy per kWh including average demand charges.  Please consider the rising energy prices.

Investment Cost

Enter the estimated additional cost of purchasing and installing a variable speed AC drive as compared to the alternative method of flow control used in the comparison. Use the same currency units as entered for energy cost. This entry will be used to calculate the direct payback time.  If the existing system needs costly maintenance cost compute the net present value of those and deduct from investment amount.

CO2 emission (kg/kWh)

This value shall reflect the local conditions: the emission per kWh. 

Results 

The results of the calculations include the estimated annual energy consumption for the existing control method and for AC drive control, the difference of these two, which equals the annual energy saving.  

FanSave also estimates the reduction in carbon dioxide (CO2) emissions due to the reduced electricity consumption. 

Payback period is calculated for the investment in the drive as compared to the alternative method of flow control. 

[image: image5.png]Annual energy saving 70 Mwh
Annual energy consumption:

with existing cortrolmethod 185 wwn
with improved controlmethod 15 wwn

Saving percertage B0 %

Energy consumptionkWh

45000

40000

35000

2

BOutlet damper BAC Drive:

i
i
H
H

-
o
i
e
e I
m
o .
R R e

Flowse

casaBRERE

8
8

) E)

——Outetdsmper  ——ACDWE

Economic data
Annual saving 7030
Payback period 04 vears

‘Annual CO2 recuction 28 tyear

) 100
Flowse




Figure 2 FanSave results page
Calculated savings 

Annual energy saving (MWh)

This is the energy difference in favor of frequency converter control. 

Energy consumption (MWh)

These are shown for both with existing control method and new control methods.  

Saving percentage

The reduction in electricity costs in percents. This is also, of course, the energy saving in percents.

Energy consumption – graph (kWh)

The calculated energy used annually with the two control methods are shown as function of flow.

Power consumption – graph (kW)

The calculated power demand with the two control methods are shown as function of flow.

Economic results

Annual Saving

This is how much money you save thanks to the variable speed control by AC drive annually.  Money saving comes in the form of smaller electricity bill.

Payback period

This direct payback time shows how soon the savings cover the investment cost.

Annual CO2 reduction (t/year)

This is the reduction in tons per year, which results from the reduced energy consumption due to variable speed control. 

5 — Explanation of Calculations

Fan performance curves

Fan performance can be defined from its performance curves i.e. pressure curve (Qv/ptF-curve) and power curve (Qv/PR-curve). Different fan types have different shaped performance curves. Additionally, the position of the curves depends on gas density and rotation speed. For these reasons, the performance curves are often presented as sets of curves with different parameters. The manufacturer of the fan provides these performance diagrams.

The pressure curve of the fan can also be referred to as the fan curve. The suitability of a fan to a certain duct system depends partly on the form of the fan curve. All the calculations of FanSave are based on parabolic fan curve.

The useful mechanical power transferred into the volume flow is called air power PF. It is proportional to the gas volume flow, compression factor and total fan pressure.   For low pressure fans the compression factor ( 1.

The impeller power PR (also called shaft power), i.e. the mechanical power necessary for rotating the fan is then obtained by taking the fan efficiency into account. For all centrifugal fans the impeller power increases as the volume increases. This connection is presented in the power curve of the fan. 

Further on, the electric fan power is calculated by taking the motor and drive efficiencies into account.











System curve

All the duct systems have their special performance curve, system curve,

dependent on the resistances in the duct. In a turbulent flow, all the resistances caused either by friction or various duct elements are proportional to the square of the volume flow. From this follows that the resistance of the duct system, i.e. system curve, often complies with the same rule. 

Especially in industrial processes it is likely to encounter also system curves with an additional constant pressure and previously mentioned changing pressure. The calculations of FanSave are based and valid on the basic system curve without any constant pressure. 

When adjusting the fan speed to control the volume flow, the process moves via system curve (a). Respectively, when throttling the duct the fan operates continuously at the same speed, and the movement of the process is via fan curve (b). 

Control methods

For FanSave calculations the most important control methods to control the

fans during operation have been selected. Fig.4 below shows the relationship of the electric fan power compared to the volume flow in connection with these control methods. The control method presentations are average examples used in calculations.

[image: image6.png]P = f{flow)

1.1 9

1 4

0.9 1

0.8 1

0.7 4

0.6 +

0.4 4

0.3 1

0.2 1

0.1 1

-

Damping
............... 1-speed vane
[, 2-speed vane
........ Pitch

Frequency
converter
control

30
40—
50
60
70
80
90T

100

—  Flow [%]




Figure 1 The power curves of flow control methods.

Efficiencies

The given values are used in the formulas. Further, as shown in the formulas, the efficiency of the system depends on the given efficiencies of fan, mechanical transmission, motor and drive, and on the adjustment method specific correcting factor.  These correcting factors have been derived empirically.

FanSave calculations

The following formulas are used for power calculations:

The impeller power i.e. nominal shaft power of a fan is calculated 

from the formula


[image: image7.wmf]ptF

Qvn

kp

Pf

×

×

=


where kp is compression factor


[image: image8.wmf][

]

pta

nk

ptF

kp

×

×

-

=

35

.

0

1


The electrical power for different control methods, and for different flow rates 

is calculated as follows.

Frequency converter control nominal power


[image: image9.wmf]nd

nm

nt

nk

Pf

Pvs

×

×

×

=

100

, where

where 
nk =fan efficiency


nt = transmission efficiency


nm= motor efficiency


nd=drive efficiency

The power consumption on lower flow levels are tabulated 

	Flow
	Multiplier

	0.2
	0.035

	0.3
	0.055

	0.4
	0.095

	0.5
	0.155

	0.6
	0.24

	0.7
	0.37

	0.8
	0.515

	0.9
	0.74


Other control types 


[image: image10.wmf](

)

nm

nt

nk

Pf

Pd

×

×

=

100


where 
nk =fan efficiency


nt = transmission efficiency


nm= motor efficiency

The power consumption on lower flow levels are tabulated with following multipliers.

	Flow
	Slip
	Voltage
	Two speed
	Cyclic
	Inlet damper
	Pitch
	Inlet vanes

	0.2
	0.146
	0.094
	0.225
	0.2
	0.47
	0.339
	0.339

	0.3
	0.163
	0.156
	0.225
	0.3
	0.5
	0.36
	0.36

	0.4
	0.22
	0.223
	0.225
	0.4
	0.54
	0.394
	0.394

	0.5
	0.297
	0.331
	0.225
	0.5
	0.58
	0.446
	0.446

	0.6
	0.386
	0.44
	0.225
	0.6
	0.62
	0.483
	0.483

	0.7
	0.505
	0.563
	1
	0.7
	0.67
	0.559
	0.559

	0.8
	0.626
	0.703
	1
	0.8
	0.75
	0.636
	0.636

	0.9
	0.773
	0.846
	1
	0.9
	0.84
	0.763
	0.763


	Flow
	Outlet  damper F
	Outlet  damper B
	Outlet  damper R

	0.2
	0.38
	0.49
	0.49

	0.3
	0.38
	0.57
	0.57

	0.4
	0.395
	0.655
	0.655

	0.5
	0.45
	0.723
	0.723

	0.6
	0.525
	0.79
	0.79

	0.7
	0.615
	0.855
	0.855

	0.8
	0.715
	0.91
	0.91

	0.9
	0.84
	0.96
	0.96


Unit Conversions

Please use the conversion tools found on Web to work with local non SI -units.







pmax











SYSTEM CURVE











b)





p2





























PtF





a)











FAN CURVE











QV2

















QVN











Graph.1. An example of typical fan and system curves.








17
2

